## 021802010021
Specifications | JPS Requirement | [5 empty] | Supplier Response |  |  | Supporting Documentation Provided (Yes or No) | Reference and Page Number in Supporting Document. | COMMENTS
Description | TRANSFORMER, PAD MOUNTED, 3000KVA, OIL FILLED, TYPE ONAN - 65 DEGREE C RISE 3 PHASE. 23900 Grd Y13800 to 11950 Grd Y/6900
Quantity | 2 | [11 empty] | Yes
Stock Number | 21802010021 | [11 empty] | No
Manufacturer
Country Of Origin
INCO Terms
Lead Time
Warranty | The minimum warranty period shall be 18 months from date of payment or 12 months in service, whichever occurs first. The transformer shall be guaranteed for a minimum of 3 years in normal operating conditions, against any manufacturing defects or design anomalies.
3.1 Standards
3.1.2 | The Equipment being supplied shall conform to the latest editions of all relevant articles of the IEEE C57 – Power, Distribution and Regulating Transformers Standards. All applicable parts of the standards shall be observed in the design, manufacture, performance and testing.
Where equipment, components or materials are not covered by the IEEE C57 standards, relevant sections of the following standards shall apply:-
| ● | ANSI Z55.1 Gray finishes for Industrial Apparatus and Equipment.
| ● | ASTM D1816 Test method of dielectric oil
| ● | CSA C50 Insulating oil, electrical for transformers and switches.
| ● | EEMAC B6-1 Insulating mineral oil for new electrical apparatus.
| ● | NEMA TR-1 Transformers, Regulators and Reactors.
| ● | NEMA TR-P9
| ● | WUG 2.13 Rev 4
| ● | ANSI/IEEE 386-1977
| ● | NETA Inter-National Electrical Testing Association
4. Detailed Requirements
kVA | 3000
No of Phases | 3
Polarity | Subtractive
Bushings | Two (2) fuly insulated primary high voltage bushing (one (1) ot facilitate loop feed arrangement).
Fuse | The transformers shall be manufactured with a two-fuse primary protection system (bayonet fuse and current- limiting fuse), with overload indicating device
Conforming Paragraph | 4.1.1.1 | 4.1.1.2 | 4.1.1.3 | 4.1.1.4 Option 1 | 4.1.1.4 Option 2 | 4.1.1.5
Primary Voltage (kV) | 23.9KV GRD Y or 11.95KV GRD Y or 13.8KV Delta | 23.9KV GRD Y or 13.8KV Delta | 13.8/24KV GRD Y | 23.9KV GRD Y | 23.9KV GRD Y | 23.9KV GRD Y or 11.95KV GRD Y
BIL(kV) | 125
Insulation Class (kV) | 25
Secondary Voltage (Volts) | 240/415V GRDY x 240V Delta with Centre tap on one winding to provide 120V-0-120V | 240/415V GRDY x 240V Delta with Centre tap on one winding to provide 120V-0-120V | 240/415V GRDY x 240V Delta with Centre tap on one winding to provide 120V-0-120V | 6.9/11.95KV GED Y or 13.8KV Delta | 4000 GRD Y | 240/415V GRDY x 240V Delta with Centre tap on one winding to provide 120V-0-120V
BIL (kV) | 30 | 30 | 30 | 110 | 110 | 30
Insulation Class (kV) | 1.2 | 1.2 | 1.2 | 15 | 15 | 1.2
Frequency(Hz) | 50
Displacement Delta-Wye | 30o | 30o
Delta-Delta | 0o | 0o
Wye-Delta | 30o | 30o | 30o | 30o |  | 30o
Wye-Wye | 0o
Continuous rated capacity at 65℃ temperature rise | See Material Schedule for Quantities and Sizes
Taps | Two (2) 2 1⁄2% primary taps above and below normal voltage.
Impedance (Nominal) as per ANSI | 5.75% +/- 7.5%
Losses
LOSSES | Bidder shall provide guarantee average no-load and load losses as defined under the latest version of ANSI C57.12.90 unless otherwise specified. No load losses shall be provided at 850C. Load losses shall be provided at 85C as described in ANSI C57.12.90, section 9.4 “Calculation of impedance voltage and load loss from test data”. | [5 empty] | No Load |  | Full Load
4.3 Performance
4.3.1.Temperature Rise | The temperature rise measured by resistance method shall not exceed 65 ℃ at a maximum ambient temperature of 40°C when operating continuous at rated capacity.
4.3.2. Dielectric Strength | The transformers shall be designed, tested and constructed to withstand the induced voltage, the applied voltage and the impulse voltage tests in accordance with the recommendations of ANSI C57.90 for this class of transformers.
4.3.3. Overload Capacity | The transformers shall be able to carry overloads in accordance with requirements of ANSI C57.92,with moderate sacrifice of life expectancy.
4.4 Audible Sound
Audible Sound | The audible sound level of transfomers when operating at rated voltage,and measured as per ANSI C57.12.90 shall not exceed the stipulated sound levels indicated below
| Transformer Size kVA |  |  | Audible sound level dB (Max)
| 50 |  |  | 48
| 100 |  |  | 51
| 150 |  |  | 55
| 200 |  |  | 55
| 300 |  |  | 56
| 500 |  |  | 56
| 750 |  |  | 57
| 1000 |  |  | 58
| 1500 |  |  | 60
| 2000 |  |  | 61
| 2500 |  |  | 62
| 3000 |  |  | 63
| 5000 |  |  | 63
4.5 Construction
The Transformer shall be mechanically designed to ANSI requirements,unless otherwise specified
A. Dimensions | The overall dimensions of the transfomer and compartment shall be kept to a minimum. | [5 empty] | Length (mm) | Width (mm) | Height (mm)
B. Exterior finish | Modestly sculptured corners and round edges are encouraged. 1. The transformer and compartments shall be painted standard Seafoam Green or Munsell Green 70 or owner approved equivalent. Manufacturers must specify details of the paint system being offered. The insideof the compartments, the underside of the roofs and the side of the transformer facing into the compartment shall also be painted Seafoam Green or Munsell Green 70 or owner approved equivalent. 2. The finish shall conform to ANSI C57.12.28; with the exception of the salt spray test that shall be of 1500 hours duration. 3. There shall be no plates or exterior stenciling positioned on the outside of the transformer tank or switching compartment except for a small plate or decal showing the name of manufacturer and high voltage warning labels
C. Tank Compartment Assembly | 1 | Provision for lifting shall be provided and shall be adequately strengthened, sized and arranged on the tank to provide a suitable lift for the completely assembled unit. The transformer base shall be arranged so that the tank bottom does not touch the pad.
| 2 | The welding shall conform to AWS Standard.
| 3 | Diagonal break marks on large surfaces sharp edges and protruding parts shall be avoided where possible.
| 4 | The strength of the transformer shall be as such as to withstand a minimum gauge pressure of 70 kPa without leakage or permanent distortion of the tank exceeding 0.25% of the diagonal dimension of the surface so affected.
| 5 | A pentahead bolt, used in addition to a safety latch, shall be provided so that the door cannot be padlocked unless the pentahead bolt has been fastened down. The locking arrangement shall be recessed into the enclosure panel, as per ANSI C57.12.26-1987 (or latest edition) figure 11. The penta head bolt shall be held captive to prevent removal and thread damage during operation of the door including forceful closing.
| 6 | Furnished with side mounted parking stands for each high voltage bushing furnished, minimum three per phase. The parking stands in the middle for Loop Feed shall have sufficient space around them to accommodate Elastimold Cat. #163FTR or equivalent feed-thrus. Bushing spacing shall meet the minimum dimension of ANSI C57.12.26 figures 2 and 4.
| 7 | The switching compartment door shall be capable of being closed and locked when elbows of the H.V. cable and grounding elbows are inserted into the feedthru connectors.
| 8 | Provided with a pull-ring type automatic pressure relief system with means for manual operation in accordance to ANSI.
| 9 | Provided with two 25mm (1-inch) minimum brass pipe plugs or fittings for filling, draining, and pressure testing.
| 10 | Provided with a thermometer or temperature gauge, maximum indicating type.
| 11 | Provided with a magnetic type insulating fluid level gauge. The fluid gauge shall not show residual liquid when fluid is below the gauge.
D. Insulating Fluid | 1 | Furnish unused mineral oil. The dielectric strength of the fluid, when shipped inside the transformer, shall not be less than 45 kV, when tested with ASTM D1816 using 2mm electrode spacing.
| 2 | Provide insulating fluid containing no more than two parts per million of PCB’s when tested in accordance with Ontario Hydro Specification M -104M-85. The type of insulating fluid used is to be stenciled on the inside of the transformer switching compartment cover in white bold 25mm letters.
E. Drip Tray | 1 | A fixed tray, designed to retain 100ml of insulating fluid and prevent the fluid from dripping down the tank wall or onto accessories, shall be installed below the location of each withdrawable fuse. Owner approved removal oil-absorbent material shall be installed in the tray.Water running down the tank wall shall not collect in the trays.
| 2 | In all instances,the design of the withdrawable fuse assembly shall be such that repeated insertions and withdrawal of the fuse cannot result in loosening or detachment of any parts.
F. Tap Changer | All tap leads shall be brought to a tap changer inside the transformer tank. Tap changer shall be externally operated and provided with a lockable handle and plate clearly designated by number or letters the tap setting. Such designation will be easily identified with voltage of the tap shown on the name-plate.The operating handle shall be installed in the cable entrance compartment at such a location that it is visible and accessible with cables in place and handleshall be capable of being locked in any position. Tap changer will be operated only with the transformer de-energized.Tap changer shall meet requirements of ANSI C57.12.10 paragraph 9.2.1. All transformers are required to have taps of 2.5 percent and 5 percent above and below nominal rated primary voltage that shall operate on all voltage positions for muli-voltage units. The tap position must be clearly identified in the cable compartment by a suitable method such that,the identification marks provided and furnished with a separate warning sign mounted close to the operating handle,cannot be removed under any operating conditions and last the life of the transformer under normal operating conditions.Letterings are to be 15-25 mm high.
G. Connections and Terminations | Each unit shall be supplied with terminals for loop feed pad-mounted transformers.Six high-voltage bushing wells equipped with parking stands shall be supplied. Low-voltage bushings and high-voltage bushing wells shall be replaceable without removing the core and coil assembly from the tank.
| 1. High Voltage Terminations | Each transformer shall be equipped with Six (6)200A fully insulated high- voltage bushing wells complete with inserts, two per phase, tofacilitate testing.The bushing well shall be Elastimold catalogue #K1601PC-S1 (or-T1) or approved equivalent and the insert Elastimold catalogue #2701A4 or approved equal. The high-voltage neutral of the GrdY primary shall be brought out the tank wall through an insulated neutral bushing designated Ho to facilitate testing. The Ho terminal is not to be grounded internally to the tank wall. The neutral terminal shall be connected externally to the grounding spade terminal, which is grounded to the transformer tank cover or wall (see section 3.4).
| 2. Low Voltage Terminations | Each transformer shall be equipped with either four (4) or seven (7) low-voltage tinned copper terminals of the spade-type, in accordance with ANSI Standards. The secondary terminals shall be capable of withstanding a minimum vertical cantilever force of 750N continuously applied at the outermost hole of the terminal without any fluid leakage,damage or permanent distortion to the teminal. The low-voltage neutral shall be connected to an insulated neutral terminal designated Xo having a current-carrying capacity equal to the other low- voltage terminals. The Xo terminal is not to be grounded internally to the tank cover or wall. Low voltage bushings, 2.3 kV and above, shall be equipped with solderless connectors sized as in paragraph above. Low voltage bushings, 600 volts and below, shall be equipped with spade type terminals, NEMA drilled. Spade size and ampacity to be determined by transformer rating. Clamp type terminals, complete with non-ferrous bolts, nuts, washers, and lock washers for attaching these terminals to the spade shall be furnished. The clamp type terminals shall be of the “Cable Range” type with maximum range exceeding the ampacity of cable(s) required to continuously carry full load to the transformer, and shall be suitable for either copper or aluminum conductors. All Transformers having seven (7) low voltage terminals shall come configured and connected with suitable connectors for 240V DELTA. All connectors for reconfiguring the secondary for 240/415V GRDY shall be supplied separately, attached to the transformers via suitable straps.
| 3. Grounding | A copper ground bus shall be mounted horizontally in the cable compartment on the lower front of the tank wall.The ground bus shall be drilled with four 15-mm diameter holes to allow ground connections.
H. Nameplate,Labels and Markings | 1. Nameplate | The transfomer shall be provided with a nameplate containing all infomation,connection diagrams,etc.,in accordance with ANSI C57.12.00 paragraph 5.12.2.Nameplate shall be bar coded. In addition to the information to be contained in the combination nameplate and connection diagram as outlined in ANSl,the nameplateshall contain the following information: -Jamaica Public Service Company Ltd. Purchase Order Number -Total weight of the insulating liquid in kilograms -Total volume of the insulating liquid in litres -PCB content -Protective devices information The transformer nameplate and connection diagram shall be mounted on the cable entrance compartment of the transformer and shall be engraved such that the lettering will last the life of the transformer
| 2. Warnings and Labels | a. Switching Compartment Plate | Each of the high voltage switches shall have a nameplate stating, “3 Phase gang-Operated Switch” and with markings identifying its purpose (i.e. Loop Feed A, Loop Feed B and Transformer Switch). The “OPEN” and “CLOSE” positions of each switch shall also be clearly identified. The switch designations shall be clearly marked on the switch with the 25mm high lettering that will be legible for the life of the transformer under normal usage.
|  | b. Warning Label -Tap Changer | A warning sign shall be mounted close to withdrawable bayonet fuse hoder handle and shall have engraved on it in bold 10 mm minimum letters in red over white background: OPERATE TAP CHANGER SWITCH ONLY WHEN TRANSFORMER IS DE-ENERGISED. Centre lettering vertically and horizontally with 3mm between lines.
|  | c. Warning label -Withdraw able fuse | A warning sign shall be mounted close to the withdrawable bayonet fuse holder handle and shall have engraved on it in bold 10mm minimum letters in red over white background: DO NOT OPERATE FUSE ASSEMBLY UNLESS TRANSFORMER IS DE-ENERGISED. OPERATE PRESSURE RELIEF DEVICE FIRST BEFORE PULLING OUT BAYONET FUSE HOLDER. Centre lettering vertically and horizontally with 3mm between lines.
|  | d. Hazard Warning Labels | Hazard warning signs confoming to EEMAC Standard L16-1 shall be afixed to the inside and outside of the compartment doors
| Exterior Markings | A self-adhesive tag shall be externally attached to the side of the transformer in the upper left corner. it shall contain the following information: -Serial number -kVA -Manufacturer's Name/Logo - kV - Stock code number
| High Voltage and Low Voltage Terminal Markings | The high and low voltage terminals shall be stenciled H1, H2, H3, H0 and X1, X2, X3, X0 respectively in minimum 60mm high white lettering.
Cores
Cores shall be four (4) or five (5) leg cores made from cold rolled silicon steel with preferred grain orientation.
I.Transformer Insulating Oil Preservation System and Oil | The transformer shall be equipped with “Sealed Tank” Insulation Oil Preservation System and new, unused mineral oil meeting the requirements of ANSI C57.12.00 paragraph 6.6.1 (a). No further drying shall be required before putting the unit into operation.
J. Earthling Pads and Terminals | Tank grounding or earthling pads shall be provided according to ANSI C57.12.10 paragraph 9.28.One terminal suitable for both aluminum and copper conductors to permit the earthling of the transformer shall be furnished for range of sizes from 50 mm²to 120 mm² (1/0 AWG to 250 KCMIL)conductor
Accessories
All standard accessories required by ANSI shall be furnished, in size and location on the units as detailed in ANSI C57.12.10 paragraph 9.2. Each transformer shall be equipped with the following accessories:
1. Pressure Relief Device | An automatic pressure relief device (a valve or its equivalent), with means of manual operation, is mandatory. If a valve is used it shall have a minimum flow rate of sixteen (16) L/S at a gauge pressure of 100kPa. The opening pressure of the relief device shall be less than the withstand pressure of the tank structure.
2. High Voltage Load Break Switch | The transformer shall contain three (3) high voltage three-phase gang-operated, liquid-immersed, load break switches - two for the loop feed and one for the transformer primary winding tap (see Figure 1). The high voltage switch handles shall be installed inside the transformer tank with the operating handles extending into the high voltage compartment. The operating handle of the transformer switch shall be located away from the handles of the other two switches. Each switch shall be operable with a switch stick by an operating personnel standing in front of the compartment. The operating handles shall be capable of locking with a standard ANSI/IEC padlock in all positions. The manufacturer shall allow sufficient spacing between the loadbreak switches or locating them such that a low insulating fluid level will not cause a flashover between switches or between phases.
The switches shall have the following minimum electrical characteristics:
| a) Voltage class |  |  | 25 kV
| b) BIL |  |  | 150 kV
| c) Continuous and Loadbreak current: |  |  | 300A
| d) Interrupting Current: |  |  | 300A
| e) Momentary,10 cycle |  |  | Current: 12,000A ms.sys
(X/R ratio =30) 19,200A ms.asym
| f) Close and Latch Current: |  |  | 12,000A ms.sys
(X/R ratio =30) 19,200A ms.asym
| g) Operating Temperature: |  |  | 17℃ to 120℃
The contact speed of the switches shall be independent of operator speed.
Protective Devices
Each phase of the transformer shall be protected by a two-fuse protection system consisting of a replaceable bayonet fuse and an under oil, partial range, back-up current limiting fuse. The back-up current limiting fuse of dual voltage transformer shall have voltage rating suitable for the higher voltage and current rating adequate for the lower voltage. Expulsion fuses for both voltages and corresponding currents shall be provided. The lower voltage-rating fuse shall be installed, unless otherwise specified. The locking clips of the fuse holders, when locked in any position shall not be damaged when closing the transformer hood. The fuse rating and manufacturer’s Cat. No. of the bayonet fuse and current limiting fuse shall be identified on the combination nameplate. The overall arrangement of the load break and protective devices shall allow loop feed to the transformer and prevent closing of the switch unto internal faults. In addition to standard accessories the following shall be furnished: Provision for Pressure gauge.
TESTS
All Routine Tests defined in latest ANSI C57-12.00 section 8 shall be made in accordance with ANSI C57.12.90 by and at the expense of the manufacturer. Routine/Production Tests The manufacturer shall carry out all the standard Routine/Production Tests and, before shipment; the manufacturer shall furnish certified copies of the test results for approval. No transformer shall be shipped until tests results are approved. The manufacturer shall furnish certified copies of the test results for approval. No transformer shall be shipped until tests results are approved.